Indoor Ambient Solar-Powered Wireless Environmental Sensor Node Temperature · Humidity · CO₂ (opt.) · TVOC (opt.) · Light ¦ Long-Range Wireless ¦ Zero Maintenance

OVERVIEW

The Temco Controls Indoor Ambient Solar-Powered Sensor Node is a maintenance-free wireless monitoring solution designed for buildings where running wire is impractical. It collects temperature, humidity, and optional CO₂, TVOC, and light data, then transmits all readings wirelessly via long-range radio to a paired Temco gateway.

What makes this sensor unique is its specially tuned indoor solar cell. Unlike conventional solar panels designed for high-intensity outdoor sunlight, this cell is optimized for the frequency spectrum of indoor ambient light — including LED and fluorescent sources. As long as there is ordinary indoor lighting, the sensor charges and operates without batteries or maintenance.

Energy is stored in a supercapacitor (or hybrid supercapacitor), not a rechargeable battery. This eliminates the need for battery replacement and allows the sensor to be shipped and installed without hazardous materials restrictions. Buildings can deploy large numbers of sensors with zero ongoing maintenance burden.

The paired Temco gateway receives all wireless data and makes it available over BACnet and Modbus — the two dominant protocols in commercial building automation — as well as Ethernet and Wi-Fi. Data is logged to a SQL database through T3000, Temco's free, open-source software, which also supports trend graphing, floor-plan overlays, and email/alarm notifications.

KEY HIGHLIGHTS

- Specially tuned indoor solar cell — operates under LED and fluorescent light (no outdoor sunlight required)

- Supercapacitor energy storage — no batteries, no maintenance, no shipping restrictions

- Long-range wireless — penetrates 10+ floors of wood or concrete construction; > 1 km in open air

- Monitors temperature, humidity, CO₂* and TVOC* (optional), and ambient light level (* optional sensors)

- Mounts anywhere indoor light is present — truly ad-hoc, cable-free installation

- Gateway reports data over BACnet and Modbus to any standard building automation system

- Dual-interface gateway — Ethernet and Wi-Fi connectivity

- T3000 software is free and open-source — unlimited sensor trending, SQL logging, floor-plan views

- Email and alarm notifications when sensor thresholds are exceeded

- Onboard CPU intelligently manages power — automatically reduces reporting rate in low-light conditions

SENSOR SPECIFICATIONS

All sensor data is transmitted wirelessly via long-range radio. There are no wired signal outputs.

| Sensor | Range | Accuracy | Output / Interface | Response Time | Drift / Year |
| --- | --- | --- | --- | --- | --- |
| Temperature | -30 to +70 °C | ±0.2 °C (5–60 °C) | LoRa wireless | < 10 s | < ±0.1 °C |
| Relative Humidity | 0–100% RH | ±2 % (0–90 %) | LoRa wireless | < 10 s | < ±0.5 %/yr |
| CO₂ (optional) | 380–32,000 ppm | ±(100 ppm + 10%) | LoRa wireless | 20 s (τ63%) | < 1 ppm/yr |
| TVOC (optional) | 0–60,000 ppb | Qualitative IAQ index | LoRa wireless | < 30 s | — |
| Ambient Light | 0–100,000 lux | ±10 % | LoRa wireless | < 200 ms | — |

* CO₂ and TVOC are optional sensors. TVOC readings are expressed as an Indoor Air Quality (IAQ) index based on total volatile organic compounds measured by a production-calibrated Sensirion SGP sensor.

GATEWAY & RADIO SPECIFICATIONS

The sensor node requires the Temco gateway (contact Temco for current model name and ordering info). The gateway and sensor node are paired and work exclusively together — this is not a standard open protocol connection, ensuring reliable and secure communication.

| Parameter | Value | Notes |
| --- | --- | --- |
| Wireless Protocol | Long-Range (LoRa) | Sub-GHz, high penetration |
| TX Power | Up to 22 dBm | Configurable |
| Range — Open Air | > 1 km | Line of sight |
| Range — Through Floors | Up to 10+ floors | Wood/concrete; rebar may vary |
| Gateway Connectivity | Ethernet + Wi-Fi | Dual interface |
| Protocols Supported | BACnet, Modbus | Industry standard building automation |
| Max Sensor Nodes | Contact Temco | Multi-node support |
| Operating Temperature | -40 to +85 °C | Electronics rating |
| Supply Voltage | 3.0 – 3.6 V (typ. 3.3 V) | Internal regulated |
| Energy Storage | Supercapacitor / Hybrid | No battery — zero maintenance |
| Darkness Hold-up Time | TBD (confirm w/ hardware test) | Depends on reporting interval |

INDOOR SOLAR & ENERGY STORAGE

Conventional solar panels are tuned for the 400–700 nm visible spectrum at high irradiance (direct sunlight, ~1000 W/m²). Indoor LED and fluorescent lighting operates at much lower irradiance (~100–500 lux) with a shifted spectral profile. The solar cell in this sensor is specifically designed and tuned for these indoor-light frequencies, maximizing energy harvest under typical office, warehouse, or corridor lighting conditions.

Energy is stored in a supercapacitor or hybrid supercapacitor — not a lithium battery. Key advantages:

- No battery replacement ever required

- Compliant with shipping regulations that restrict lithium batteries

- Acceptable in buildings with strict battery/chemical policies

- Automatically reduces reporting frequency when stored energy is low, then resumes normal operation when light returns

HOW IT WORKS — TYPICAL OPERATION

| # | Step |
| --- | --- |
| 1 | Indoor ambient light charges the supercapacitor (no battery required) |
| 2 | Sensor node remains in deep low-power mode to maximize hold-up time |
| 3 | At the configured interval the node wakes up automatically |
| 4 | Active sensors are powered on; data is collected (temperature, humidity, CO₂*, TVOC*, light) |
| 5 | Data packet is sent wirelessly via long-range radio |
| 6 | Gateway receives the packet and maps values to T3 controller inputs |
| 7 | Data is available over BACnet, Modbus, Ethernet, or Wi-Fi |
| 8 | T3000 software logs readings to SQL database; alerts can be configured |

The gateway exposes all sensor inputs to the T3 controller environment. From there, values flow over BACnet (common in HVAC/commercial buildings) or Modbus (common in industrial systems) to any connected building management system. T3000 can log an unlimited number of sensor readings for an unlimited duration — storage capacity is only limited by the connected hard drive.

T3000 SOFTWARE — FREE & OPEN SOURCE

- Download and use T3000 at no cost — no license fees, no subscriptions

- Live dashboard: view all sensor values in real time

- Trend logging: SQL database backend handles millions of records for large installations

- Floor-plan views: place sensor icons on building drawings and see live values

- Unlimited sensors, unlimited history (disk-space permitting)

- Email and push alerts: notify maintenance staff when CO₂, temperature, or humidity exceed setpoints

- All data accessible via BACnet and Modbus for integration with third-party BMS platforms

INSTALLATION & COMMISSIONING

Installation is straightforward — mount the sensor anywhere it receives consistent indoor light, then pair it with the Temco gateway.

- Mount the sensor node where indoor ambient light is present (ceiling, wall, or column)

- Avoid locations in permanent shadow unless a larger energy storage option is specified

- Power the Temco gateway and connect it to the network via Ethernet or Wi-Fi

- Pair the sensor node to the gateway using the firmware pairing procedure (see gateway setup guide)

- Confirm live values appear in T3000 before enabling trend log recording

- For long-term validation: record supercapacitor voltage, reporting interval, and packet reception quality over 24–48 hours

Note: sensor configuration, reporting interval, and power behaviour may vary by firmware version. Contact Temco Controls for current firmware documentation.

ORDERING INFORMATION

Contact Temco Controls for current part numbers, gateway model designation, optional sensor configurations, and volume pricing.

temcocontrols.com