Temco Controls

Solar-Powered LoRa Environmental Sensor Node

RA-08 Wireless Sensor Node for T3 Controller Gateway

Preliminary Product Datasheet

Document Revision: 0.2   |   Status: Draft for Review

This document describes a solar-powered, cable-free LoRa environmental sensor node that sends remote environmental data to a T3 controller RA-08 gateway and a central BACnet system.

| Item | Description |
| --- | --- |
| Product Type | Solar-powered, cable-free wireless environmental sensor node |
| Wireless Link | RA-08 LoRa communication |
| Gateway | T3 controller with RA-08 LoRa gateway module |
| Measured Data | Temperature, humidity, CO2, TVOC, light level, and power status |
| Software Integration | T3000 live monitoring and trend logs |
| Unique Value | Install sensors almost anywhere without power or communication cables, then report the data to a central BACnet system. |

1. Product Overview

The Temco Controls Solar-Powered LoRa Environmental Sensor Node is a cable-free wireless sensing solution for locations where running power or communication cables is difficult or expensive. Based on the RA-08 LoRa module, each solar-powered node can be installed close to the measurement point, collect environmental data such as temperature, humidity, CO2, TVOC, and light level, and transmit that data wirelessly to a T3 controller equipped with an RA-08 LoRa gateway module.

The sensor node is powered by a solar panel and uses a supercapacitor as the energy storage device. To reduce power consumption, the node keeps most sensors powered off during standby, wakes up periodically, enables the required sensors, collects data, sends the LoRa packet, and then returns to low-power mode.

The T3 controller gateway converts these remote wireless points into usable controller data and exposes them to the central BACnet system and T3000. This allows sensors to be installed almost anywhere without pulling sensor cables back to the controller, which is a unique value point compared with conventional wired sensing products.

2. System Architecture

| System Block | Function |
| --- | --- |
| Solar Sensor Node | Measures temperature, humidity, CO2, TVOC, light level, and power status. |
| LoRa Wireless Link | Transmits sensor data to the gateway using the RA-08 LoRa module. |
| T3 Controller Gateway | Receives LoRa packets through the RA-08 gateway module, updates controller values, and exposes the data to BACnet. |
| T3000 Software | Displays live data, records trend logs, and supports controller configuration. |
| Building Automation System | Uses controller data through the supported network interfaces and protocols. |
| Central BACnet System | Receives the mapped values from the T3 controller as part of the BACnet building automation network. |

Typical data path: Solar Sensor Node -> LoRa Wireless Link -> T3 Controller with RA-08 Gateway -> Central BACnet System / T3000 / Trend Logs

3. Key Features

Cable-free sensor installation for remote, outdoor, rooftop, greenhouse, and retrofit locations

Reports remote sensor data to a central BACnet system through the T3 controller RA-08 gateway

Reduces the need for field wiring between sensor locations and the controller

Solar-powered wireless environmental sensor node

RA-08 LoRa long-range wireless communication

Supports temperature, humidity, CO2, TVOC, and light sensing

Supercapacitor-based energy storage

Low-power firmware design with periodic wake-up and reporting

Sensor power control to reduce standby current

Designed to work with a T3 controller RA-08 LoRa gateway

Sensor data can be displayed and recorded in T3000 trend logs

Suitable for remote or hard-to-wire monitoring locations

4. Typical Applications

Greenhouse and smart agriculture monitoring

Outdoor environmental monitoring

Remote air quality sensing

Building perimeter or rooftop sensor points

Solar-powered IoT terminals

Locations where power wiring or communication cabling is difficult

5. Sensor Data

| Parameter | Description |
| --- | --- |
| Temperature | Ambient temperature measurement |
| Humidity | Relative humidity measurement |
| CO2 | Carbon dioxide concentration |
| TVOC | Total volatile organic compounds |
| Light Level | Ambient light intensity |
| Power Status | Optional solar input, supply voltage, or supercapacitor voltage monitoring |

Note: The actual sensor configuration may vary depending on the product version.

6. Power Design

The device is designed for low-power solar operation. During normal operation, the node wakes up at a configured interval, powers the sensors, takes measurements, transmits the data through LoRa, and then returns to low-power mode.

| Item | Description |
| --- | --- |
| Power Source | Solar panel |
| Energy Storage | Supercapacitor |
| System Voltage | 3.3 V typical |
| Sensor Power Control | Individual sensor enable control where supported by hardware |
| Operating Mode | Periodic wake-up, measurement, LoRa reporting, then sleep |
| Standby Mode | Low-power sleep mode |

The final operating time depends on solar panel size, lighting conditions, reporting interval, sensor configuration, firmware settings, and supercapacitor capacity.

7. Wireless Communication

| Item | Description |
| --- | --- |
| Wireless Module | RA-08 LoRa module |
| Wireless Protocol | Temco LoRa sensor protocol |
| Gateway | T3 controller with RA-08 LoRa gateway module |
| Data Direction | Sensor node to T3 RA-08 gateway, then to central BACnet/T3000 system |
| Typical Data | Temperature, humidity, CO2, TVOC, light level, and power status |
| Reporting Interval | Firmware configurable |
| System Integration | Remote wireless sensor values are mapped into the T3 controller for BACnet/T3000 use. |

8. T3 Controller Gateway Integration

The RA-08 gateway installed in the T3 controller receives wireless packets from the solar sensor nodes. The received values can be mapped into the T3 controller system, exposed to the central BACnet system, and viewed or logged through T3000.

Receives LoRa sensor data from multiple remote nodes

Displays live sensor values in T3000

Records sensor data in T3000 trend logs

Allows received values to be used in controller logic, depending on firmware support

Provides a bridge between wireless sensor nodes and the central BACnet building automation system

9. Main Electrical Characteristics

| Parameter | Min | Typ | Max | Unit | Notes |
| --- | --- | --- | --- | --- | --- |
| System Supply Voltage | 3.0 | 3.3 | 3.6 | V | Internal regulated supply |
| LoRa TX Power | - | 20 | 22 | dBm | Depends on module configuration |
| Operating Temperature | -40 | - | +85 | deg C | Electronics rating; sensor limits may vary |
| Sleep Current | TBD | TBD | TBD | uA | To be confirmed by testing |
| Active Sensor Current | TBD | TBD | TBD | mA | Depends on enabled sensors |
| LoRa TX Current | TBD | TBD | TBD | mA | Depends on TX power and radio configuration |

TBD values should be replaced after hardware power-consumption testing is completed.

10. Internal Interface Signals

| Signal | Function |
| --- | --- |
| I2C_SCL | I2C clock for environmental sensors |
| I2C_SDA | I2C data for environmental sensors |
| CO2_EN | CO2 sensor power enable |
| SHT40_EN | Temperature/humidity sensor power enable |
| TVOC_EN | TVOC sensor power enable |
| LIGHT_EN | Light sensor power enable, if used |
| LED | Status indicator |
| SOLAR_IN | Solar panel input |
| CAP | Supercapacitor connection |

11. Typical Operation Sequence

The solar panel charges the supercapacitor during available light.

The node remains in low-power mode most of the time.

At the configured interval, the node wakes up.

Sensor power is enabled.

Temperature, humidity, CO2, TVOC, and light data are collected.

The node sends the data packet through LoRa.

The T3 RA-08 gateway receives the packet.

The T3 controller updates the corresponding values.

T3000 can display and record the data in trend logs.

The node returns to low-power mode.

12. Installation and Commissioning Notes

Install the node where the solar panel can receive sufficient light for the required reporting interval.

Avoid mounting locations with long periods of shade unless a larger energy storage device is used.

Verify that the T3 controller has the RA-08 gateway module installed and configured.

Confirm that the node is joined or assigned according to the firmware pairing procedure.

Check live values in T3000 before enabling trend log recording.

For long-term testing, record solar input, supercapacitor voltage, reporting interval, and packet reception quality.

13. Ordering Information

| Model | Description |
| --- | --- |
| RA08-SOLAR-ENV | Solar-powered LoRa environmental sensor node with temperature/humidity, CO2, TVOC, and light sensing |
| RA08-GW-T3 | RA-08 LoRa gateway option for T3 controller |

14. Notes

Sensor configuration, reporting interval, and power behavior may vary by firmware version.

Solar performance depends strongly on installation location and available light.

Final current consumption and operating duration should be confirmed with production hardware testing.

This product is intended to work as part of the Temco T3 controller, T3000, and BACnet building automation ecosystem.

15. Revision History

| Revision | Date | Description |
| --- | --- | --- |
| 0.2 | May 2026 | Updated cable-free sensor and central BACnet positioning. |